expand / automatic reclosing devices

Remote actuator, 4 MW (module width), 24 V AC/DC, RCCB: In max. 63 A, Switch-on attempts: 1

The remote actuator is a retro-fittable unit for the remote control and monitoring of residual current circuit-breakers from series DFS 2/DFS 4.  
Auxiliary switch contacts constantly indicate the current status of the residual current circuit-breaker and the remote actuator.
Number of automatic switch-on attempts: 1
max. Rated current main contact unit: 63 A
Remote release: true

control input:
Rated voltage (DC): 24 V
Rated current: 1 mA

switching output (relays):
3 NO
Rated voltage (AC): 24 V
Rated current AC (typ.): 1 A 
Rated voltage (DC): 24 V
Rated current DC (typ.): 1 A
max. Rated power: 24 VA

screw-type terminal top and bottom (control input, switching output, mains relay):
Clamping area: min. 0.4 mm² ... max. 2.5 mm²

Operating voltage (AC): 24 V (21.6 V ... 30 V)
max. Current consumption AC: 0.64 A
Operating frequency (fixed): 50 Hz
Operating voltage (DC): 24 V (21.6 V ... 26.4 V)
max. Current consumption DC: 0.5 A

Rated operating mode: continuous operation
Duty cycle: continuous operation
Operating position: optional

Housing type: distribution board housing
Installation type: Mounting rail (35 mm), Device extension
Protection class: IP20
Dimensions of transformer opening: W 72 mm (4 MW (module width)) × H 85 mm × D 76 mm

Design requirements/Standards: EN 55014, EN 63024

Factory: Doepke or similar
Item designation: DFA 2-1
Order number: 09100112
selected make/type: ___________/___________