expand / automatic reclosing devices

Remote actuator, 4 MW (module width), 230 V AC, RCCB: In max. 63 A, Switch-on attempts: 1, 3

The remote actuator is a retro-fittable unit for the remote control and monitoring of residual current circuit-breakers from series DFS 2/DFS 4.  
Auxiliary switch contacts constantly indicate the current status of the residual current circuit-breaker and the remote actuator.
Number of automatic switch-on attempts: 1, 3
max. Rated current main contact unit: 63 A
Remote release: true

control input:
Rated voltage (AC): 12 V ... 253 V
Rated voltage (DC): 20 V ... 253 V

switching output (relays):
1 NC/2 NO/1 CO
Rated voltage (AC): 253 V 
Rated voltage (DC): 253 V
max. Rated power: 60 VA

screw-type terminal top and bottom (control input, switching output, mains relay):
Clamping area: min. 0.4 mm² ... max. 2.5 mm²

Operating voltage (AC): 230 V (195.5 V ... 264.5 V)
max. Current consumption AC: 0.25 A
Operating frequency (fixed): 50 Hz

Rated operating mode: continuous operation
Duty cycle: continuous operation
Operating position: optional

Housing type: distribution board housing
Installation type: Mounting rail (35 mm), Device extension
Protection class: IP20
Dimensions of transformer opening: W 72 mm (4 MW (module width)) × H 85 mm × D 76 mm

Design requirements/Standards: EN 55014, EN 63024

Factory: Doepke or similar
Item designation: DFA 2-4
Order number: 09100115
selected make/type: ___________/___________