protect / Residual current circuit-breakers (RCCBs)

Residual current circuit-breakers, four-pole, 63 A, 0.03 A, Type A, for electromobility, N right

Mains voltage-independent residual current circuit-breaker (RCCB) for detecting AC residual currents and pulsating DC residual currents
with active mains-voltage-dependent function for detecting smooth DC residual currents and a tripping threshold of 6 mA
doubled wiring level above and below
switch position indicator and multifunction switch toggle with the functions "on", "off" and "tripped" (centre position)
viewing window for labels

Residual current type: A
Rated residual current I&Delta;n: 0.03 A
Neutral conductor position: right
Module widths: 4
Number of poles: 4
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 63 A
Rated frequency: 50 Hz 

screw-type terminal top and bottom (load circuit):
Cross section solid: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section AWG, solid: 15 ... 1
Cross section AWG, stranded: 15 ... 1
Cross section AWG, flexible: 15 ... 1
Cross section AWG, flexible with ferrule: 15 ... 1

 Ambient temperature: min. -25 °C ... max. 40 °C

Housing type: distribution board housing
Installation type: Mounting rail (35 mm)
Protection class: IP20 (installed: IP40)
Dimensions of transformer opening: W 72 mm (4 MW (module width)) × H 85 mm × D 75 mm

Certifications: VDE
Design requirements/Standards: VDE 0664-10, DIN EN 61008-1, VDE V 0664-120, EN 62955

Factory: Doepke or similar
Item designation: DFS 4 063-4/0,03-A EV R
Order number: 09144817
selected make/type: ___________/___________