protect / Residual current circuit-breakers (RCCBs)

Residual current circuit-breakers, four-pole, 63 A, 0.03 A, Type B SK, Emergency stop/remote drive, N right

AC/DC sensitive residual current circuit-breakers (RCCBs) for detecting AC, pulsating and smooth DC residual currents
sensitive to residual currents and mixed frequencies from 0 Hz to 150 kHz
fulfils the requirements of DIN VDE 0100-723 for classrooms with experimental equipment and can be switched back on via remote control

doubled wiring level above and below
switch position indicator and multifunction switch toggle with the functions "on", "off" and "tripped" (centre position)
viewing window for labels

Residual current type: B
Tripping characteristic curve: SK
Rated residual current I&Delta;n: 0.03 A

short-time delayed (lightning-resistant)
Neutral conductor position: right
Module widths: 5
Number of poles (total): 4
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 63 A
Rated frequency: 50 Hz

Auxiliary device (Emergency shut-off device):
Additional device AE1 operating voltage: 50 V ... 440 V (AC)

Auxiliary device (Remote actuator):
Auxiliary device AE2 version: Motor drive
Additional device AE2 operating voltage: 24 V (21.6 V ... 26.4 V) (DC)
max. Additional device AE2 current consumption: 2 A 

Remote actuator feedback output (semiconductor):
Rated voltage (DC): 24 V (21.6 V ... 26.4 V)
max. Rated current DC: 0.2 A

Control input (remote actuator):
Rated voltage (DC): 24 V (21.6 V ... 26.4 V)

Screw-type terminal top and bottom (load circuit):
Cross section solid: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section AWG, solid: 15 ... 1
Cross section AWG, stranded: 15 ... 1
Cross section AWG, flexible: 15 ... 1
Cross section AWG, flexible with ferrule: 15 ... 1

Screw-type terminal  (Emergency shut-off device, Remote actuator):
Clamping area: min. 0.3 mm² ... max. 1.5 mm²
Cross section AWG, solid: 22 ... 16
Cross section AWG, stranded: 22 ... 16
Cross section AWG, flexible with ferrule: 22 ... 16
 Ambient temperature: min. -5 °C ... max. 40 °C

Housing type: distribution board housing
Installation type: Mounting rail (35 mm)
Protection class: IP20 (installed: IP40)
Dimensions of transformer opening: W 89.8 mm (5 MW (module width)) × H 85 mm × D 75 mm

Design requirements/Standards: VDE 0664-10, VDE 0664-40, ÖVE/ÖNORM E 8601

Factory: Doepke or similar
Item designation: DFS 4 063-4/0,03-B SK FANA24DC R
Order number: 09144869
selected make/type: ___________/___________