protect / Portable residual current circuit breakers

PRCD module, three-pole, 40 A, 0.03 A, Type B

Base component for setting up a PRCD

Protective functions: Residual current protection, Restart protection, Anticlockwise rotating field locking, PE conductor monitoring, Undervoltage trip§§ZEnd§§ §§ZStart_L conductor interruption, N conductor interruption, PE conductor interruption (> 40 kOhm), L and PE conductor mix-up, L and N conductor mix-up, No N and PE conductor mix-up detected§§
Network fault detection: L conductor interruption, N conductor interruption, PE conductor interruption (> 40 kOhm), L and PE conductor mix-up, L and N conductor mix-up, No N and PE conductor mix-up detected§§ZEnd§§ §§ZStart_0 Hz ... 100 kHz§§
Error voltage monitoring:§§ZEnd§§ §§ZStart_25§§
Rated residual voltage: 25 V§§ZEnd§§ §§ZStart_50§§
DC tripping threshold: 50 V§§ZEnd§§ §§ZStart_0 Hz ... 100 kHz§§
Tripping frequency range: 0 Hz ... 100 kHz§§ZEnd§§ §§ZStart_50 Hz ... 60 Hz§§
PE conductor monitoring: §§ZEnd§§ §§ZStart_0.01§§
Rated external residual current ‘Hold PE’: 0.01 A§§ZEnd§§ §§ZStart_5§§
Number of poles: 5
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 40 A
Rated frequency: 50 Hz

screw-type terminal top and bottom (load circuit):
Cross section solid: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: max. 16 mm²
 Ambient temperature: min. -25 °C ... max. 55 °C

Housing type: distribution board housing
Installation type: Mounting rail (35 mm)
Protection class: IP20
Dimensions of transformer opening: W 144 mm (8 MW (module width)) × H 85 mm × D 75 mm

Factory: Doepke or similar
Item designation: DPRCD-M1
Order number: 09342100
selected make/type: ___________/___________