protect / Miniature circuit-breaker (MCB)

Circuit-breakers, three-pole, C-characteristic, 16 A@230 V, 400 V (AC) / 16 A@60 V (DC), 6 kA, for industrial facilities, with red housing

Miniature circuit-breakers (MCBs) of type DLS 6 are predominately used for overcurrent protection of cables and lines as per VDE 0100-430 and protection against electrical shock as per VDE 0100-410.
Devices of the i design are fitted with a peculiar high rated switching capacity of 6 kA for industrial applications and provide screw terminals with top and bottom strain-relief clamps.
  quick fastening for removal of multiple miniature circuit-breakers from the bottom interconnection
 large, folding label window for a secure hold and protection of the label
 use of conventional wiring rails
 ON/OFF switch position indicator on the switch toggle
 accessories retro-fittable on the right
 labelling software free of charge
 
Tripping characteristic: C
Number of poles: 3
Insulation group (250 V AC): C

load circuit (load disconnect contact):
3 NO
Number of poles (total): 3
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 16 A 
Rated frequency: 50 Hz (16.67 Hz ... 60 Hz)
Rated voltage (DC): 60 V
Rated current DC (typ.): 16 A
Rated short-circuit current: 6 kA
Rated insulation voltage: 2 kV
Rated switching capacity as of EN 60898 at 230 V: 6 kA
Rated switching capacity as of EN 60898 at 400 V: 6 kA

screw terminals with strain-relief clamp top (load circuit):
Cross section solid: 1-wire: 0.5 mm² ... 25 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 25 mm²
Connecting capacity flexible: 1-wire: 1 mm² ... 16 mm²
Cross section flexible with ferrule: 0.5 mm² ... 16 mm²

screw terminals with strain-relief clamp bottom (load circuit):
Cross section solid: 1-wire: 0.5 mm² ... 35 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 35 mm²
Connecting capacity flexible: 1-wire: 1 mm² ... 25 mm²
Cross section flexible with ferrule: 0.5 mm² ... 16 mm²

 Ambient temperature: min. -25 °C ... max. 70 °C

Housing type: distribution board housing
Installation type: Mounting rail (35 mm)
Protection class: IP20
Dimensions of transformer opening: W 53.1 mm (3 MW (module width)) × H 82.5 mm × D 74 mm

Factory: Doepke or similar
Item designation: DLS 6i C16-3 RT
Order number: 09860132
selected make/type: ___________/___________