switch / Switch-disconnectors

switch-disconnectors,  100 A, 4 NO, N right

switch-disconnectors
double-sided two-tier terminals for large conductor cross-section and busbar
Switch position indicator
Viewing window for labels

load circuit (load disconnect contact):
4 NO
Number of poles: 4
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 100 A 
Rated frequency: 50 Hz, 60 Hz
max. Total rated switching capacity: 10 kA
Rated insulation voltage: 400 V 

screw-type terminal top and bottom (load circuit):
Cross section solid: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1.5 mm² ... 35 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section AWG, solid: 15 ... 1
Cross section AWG, stranded: 15 ... 1
Cross section AWG, flexible: 15 ... 1

Design requirements/Standards: EN 60947-3, EN 60068-2-30

Factory: Doepke or similar
Item designation: DHS 4-100 R
Order number: 09900013
selected make/type: ___________/___________