switch / Switch-disconnectors

switch-disconnectors,  125 A, 4 NO, with emergency shut-off function and remote actuator

switch-disconnectors with Emergency shut-off device and Remote actuator
double-sided two-tier terminals for large conductor cross-section and busbar
Switch position indicator
Viewing window for labels

auxiliary device (Emergency shut-off device):
Additional device AE1 operating voltage: 50 V ... 440 V (AC)
auxiliary device (Remote actuator):
Auxiliary device AE2 version: Motor drive
Additional device AE2 operating voltage: 24 V (21.6 V ... 26.4 V) (DC)
max. Additional device AE2 current consumption: 2 A

Control input (remote actuator):
Rated voltage (DC): 24 V (21.6 V ... 26.4 V)
min. Pulse duration control input: 60 ms
Bounce time of push buttons: 10 ms

load circuit (load disconnect contact):
4 NO
Number of poles (total): 4
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 125 A 
Rated frequency: 50 Hz, 60 Hz
max. Total rated switching capacity: 10 kA
Rated short-circuit current: 10 kA
Rated insulation voltage: 400 V 

Remote actuator feedback output (semiconductor):
Rated voltage (DC): 24 V (21.6 V ... 26.4 V)
max. Rated current DC: 0.2 A

screw-type terminal top and bottom (load circuit):
Cross section solid: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1.5 mm² ... 35 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section AWG, solid: 15 ... 1
Cross section AWG, stranded: 15 ... 1
Cross section AWG, flexible: 15 ... 1

screw-type terminal  (Emergency shut-off device, Remote actuator):
Clamping area: min. 0.3 mm² ... max. 1.5 mm²
Cross section AWG, solid: 22 ... 16
Cross section AWG, stranded: 22 ... 16
Cross section AWG, flexible with ferrule: 22 ... 16

Design requirements/Standards: EN 60947-3, EN 60068-2-30, EN 63024, EN 55014

Factory: Doepke or similar
Item designation: DHS 4-125 FANA24DC
Order number: 09900018
selected make/type: ___________/___________