switch / Switch-disconnectors

switch-disconnectors,  63 A, 4 NO, mains monitoring with N-sensor

switch-disconnectors
Including sensor for monitoring the neutral conductor potential
double-sided two-tier terminals for large conductor cross-section and busbar
Switch position indicator
Viewing window for labels

Error voltage monitoring:
Display elements: Switch position indicator, active conductors, Network error indicator, Operating
Control elements: Switching knob, Residual current test button
Network fault detection: Phase failure, N conductor interruption, L and N conductor mix-up
Protective functions: Residual current protection
max. Switch-off time error voltage 20 V: 200
max. Switch-off time error voltage ≥ 50 V: 150
Auslösegrenze Spannungsunsymmetrie: 5 % ... 10 %
Rated residual voltage: 20
Non-trip time: 70

load circuit (load disconnect contact):
4 NO
Number of poles (total): 4
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 63 A 
Rated frequency: 50 Hz, 60 Hz
max. Total rated switching capacity: 10 kA
Rated short-circuit current: 10 kA
Rated insulation voltage: 400 V 

screw-type terminal top and bottom (load circuit):
Cross section solid: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 50 mm²; 2-wire: 1.5 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1.5 mm² ... 35 mm²; 2-wire: 1.5 mm² ... 16 mm²
Cross section AWG, solid: 15 ... 1
Cross section AWG, stranded: 15 ... 1
Cross section AWG, flexible: 15 ... 1

Design requirements/Standards: EN 60947-3

Factory: Doepke or similar
Item designation: DHS 6-063 NUS
Order number: 09900020
selected make/type: ___________/___________