protect / mobile full rubber distribution board

Full rubber distributor, Input: 16 A, Output: 16 A

Mobile full rubber distribution board with integrated residual current circuit-breaker (RCCB) type B for tripping at AC residual currents > 6 mA. The AC-DC sensitive RCCB is used to protect frequency-controlled equipment and provide personal protection when the upstream residual current device is unknown or is type A or F.

Integrated switching devices: DFS 4 B SK MI HD 30 mA
max. Conditional short-circuit current Icc: 10 kA
Rated power factor RDF: 1

supply:
Rated voltage (AC): 230 V, 400 V
Rated current: 16 A

load output:
Number of poles: 5
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 16 A 
Rated frequency: 50 Hz 

CEE plug 16 A right (supply):
Cable type: H07RN-F 5G2,5
max. Cable length: 2 m

CEE socket 16 A front (load output):
Connection design: female

Rated operating mode: continuous operation
Duty cycle: continuous operation

Housing type: full rubber housing
Installation type: portable, stackable
Protection class: IP44
Dimensions of transformer opening: W 270 mm × H 339 mm × D 280 mm

Design requirements/Standards: DGUV information 203-006 (BGI 608), IEC 61439-4, IEC 62262

Factory: Doepke or similar
Item designation: DPB 16 01-100
Order number: 09931300
selected make/type: ___________/___________