protect / residual current operated circuit-breakers with integral overcurrent protection (RCBOs) / Residual current type A

Residual current operated circuit-breaker with integral overcurrent protection, two-pole, 15 A, 0.3 A, 10 kA, C-characteristic, Type A

Mains voltage-independent residual current circuit-breaker with overcurrent protection (RCBO) for detection of AC residual currents and pulsating DC residual currents
suitable for retro-fitting of additional equipment

Tripping characteristic: C
Residual current type: A
Rated residual current I&Delta;n: 0.3 A
Neutral conductor position: left or right
Module widths: 2
Number of poles (total): 2
Rated voltage (AC): 230 V
Rated current AC (typ.): 15 A 
Rated frequency: 50 Hz
max. Total rated switching capacity: 10 kA
Rated short-circuit current: 10 kA
Rated insulation voltage: 250 V

screw-type terminal top, bottom (load circuit):
Clamping area: min. 1 mm² ... max. 25 mm²
Cross section solid: 1-wire: 1 mm² ... 25 mm²
Cross section stranded: 1-wire: 1 mm² ... 16 mm²
Connecting capacity flexible: 1-wire: 1 mm² ... 16 mm²
 Ambient temperature: min. -25 °C ... max. 40 °C

Housing type: distribution board housing
Installation type: Mounting rail (35 mm)
Protection class: IP20 (installed: IP40)
Dimensions of transformer opening: W 35 mm (2 MW (module width)) × H 80 mm × D 74 mm

Design requirements/Standards: EN 61009, EN 61009-2-1

Factory: Doepke or similar
Item designation: DRCBO 2 C15/0,30/2-A
Order number: 09934195
selected make/type: ___________/___________